# Boiler/Furnace Simulator
Class and Laboratory Exercises

Live Boiler/Furnace Transient Simulator

Mohsin Mohd Sies, HiREF, UTM - 2026

Purpose: A ready-to-use set of guided, inquiry-based exercises using the simulator’s combustion, steam-side, control, fault-injection, alarm, trend and CSV-logging functions.

# How to use this exercise pack

Exercises 1-3 establish normal operation, fuel/air relationships and transient response.

Exercises 4-7 focus on drum-level control, steam-temperature control, instrumentation and heat-transfer degradation.

Exercises 8-13 integrate emissions diagnosis, fault identification, energy accounting, inventory protection, alarm chronology and open-ended optimization.

Students should begin each exercise with Reset unless instructed otherwise, allow variables to settle, and use Trends, Diagnostics, Flue Gas and Alarms tabs as directed.

CSV logging may be enabled for quantitative work. The simulator is an educational reduced-order model; results should be interpreted as trends rather than plant-design or regulatory predictions.

# Suggested assessment

| Component | Suggested weight | Evidence |
| --- | --- | --- |
| Preparation and correct setup | 15% | Initial conditions and selected modes |
| Data quality | 25% | Tables, plots or exported CSV |
| Physical interpretation | 35% | Explanation of cause-and-effect trends |
| Diagnosis and recommended action | 15% | Fault reasoning and operator response |
| Clarity and reflection | 10% | Concise conclusions and limitations |

Exercise 1: Establishing a Stable Boiler Operating Point

| Suggested duration | Format | Difficulty |
| --- | --- | --- |
| 30-40 min | Individual or pairs | Introductory |

## Learning objectives

Identify the simulator’s principal combustion, steam-side and control variables.

Recognize a stable operating point from trends and indications.

Explain the relationships among O2, efficiency, drum level, steam temperature and feedwater flow.

## Initial setup

Click Reset.

Use Natural Gas with preset composition locked.

Keep Auto O2 trim, Auto cascade steam-T, Density compensation, Bumpless switching and Coordinated firing enabled.

Use Auto-select drum-level mode and 1x speed.

## Procedure

Start the simulator and allow the plant to settle for at least 40 simulated seconds.

Record the active drum-level mode and the steady values listed below.

Open each Notebook tab and identify what information it contributes.

Pause the simulator and write a one-paragraph description of normal operation.

## Data to record

| Variable / observation | Recorded value / notes |
| --- | --- |
| Active level-control mode |  |
| Dry O2 (%) |  |
| Boiler efficiency (%) |  |
| Drum level (%) |  |
| Steam flow and feedwater flow (kg/s) |  |
| Steam outlet temperature (C) |  |
| Stack temperature (C) |  |
| Dew-point margin (C) |  |
| Alarm and trip status |  |

## Analysis and discussion questions

Why should steam flow and feedwater flow be close during steady operation?

Why does the displayed drum level not need to be exactly equal to the setpoint at every instant?

Which three indications give the quickest confirmation that combustion is healthy?

What evidence shows that the controllers are operating rather than the plant being static?

## Expected qualitative behaviour

O2 approaches its setpoint, drum level remains near its setpoint, and no trip occurs.

Steam and feedwater flows remain approximately balanced.

Steam temperature approaches its setpoint with limited spray demand.

The active mode may be three-element or an automatic selection consistent with the operating condition.

Exercise 2: Excess Air, O2, CO and Efficiency

| Suggested duration | Format | Difficulty |
| --- | --- | --- |
| 45-60 min | Pairs | Introductory |

## Learning objectives

Relate excess air to dry O2, CO2, CO, stack temperature and efficiency.

Identify the practical compromise between air-starved and excessive-air operation.

Use the combustion map to interpret an operating path.

## Initial setup

Reset and start from stable operation.

Disable Auto O2 trim so the Excess air base control can be changed directly.

Keep burner mixing at 95%, air leakage at 0% and fouling at 0%.

## Procedure

Set excess air successively to 0%, 5%, 15%, 30% and 45%.

At each setting, allow the analyzer and plant variables to settle.

Record O2, CO2, CO, efficiency and stack temperature.

Return to 15%, enable Auto O2 trim and observe recovery toward the O2 setpoint.

## Data to record

| Variable / observation | Recorded value / notes |
| --- | --- |
| Excess air (%) |  |
| Dry O2 (%) |  |
| Dry CO2 (%) |  |
| Dry CO (ppm) |  |
| Efficiency (%) |  |
| Stack temperature (C) |  |
| Flue-gas diagnosis |  |

## Analysis and discussion questions

At which setting does CO rise sharply?

Why can very high excess air produce low CO but poorer efficiency?

Why does CO2 tend to be diluted as excess air increases?

Which single measurement would be misleading if used without the others?

State an operating region that balances clean combustion and efficiency in this model.

## Expected qualitative behaviour

Near-stoichiometric or air-deficient firing produces low O2 and strong CO breakthrough.

Increasing excess air suppresses CO but raises dry O2 and generally increases stack loss.

Efficiency exhibits an optimum rather than increasing continuously with air.

Automatic O2 trim moves the plant back toward the configured O2 target.

Teaching note: The exact numerical optimum is model-dependent. Grade the explanation of trends more heavily than a particular value.

Exercise 3: Fuel Change and Fuel-Quality Disturbance

| Suggested duration | Format | Difficulty |
| --- | --- | --- |
| 45-60 min | Groups of 2-3 | Introductory |

## Learning objectives

Compare the response of different gaseous or liquid fuel surrogates.

Explain how composition and LHV affect fuel rate, air requirement and steam capability.

Distinguish a fuel-quality change from a demand change.

## Initial setup

Reset.

Keep coordinated firing and all main automatic controls enabled.

Select three fuels from Natural Gas, Hydrogen, Biogas, LPG and Diesel Surrogate.

## Procedure

For each fuel, load the preset and run to a reasonably settled condition.

Record the fuel unit, actual fuel flow, stoichiometric air, dry O2, steam capacity and efficiency.

For one fuel, click Fuel quality -5% twice and observe adequacy and fuel/feedwater warning behaviour.

Restore the fuel preset and compare recovery.

## Data to record

| Variable / observation | Recorded value / notes |
| --- | --- |
| Fuel name and phase |  |
| Fuel flow unit |  |
| Actual fuel flow |  |
| Stoichiometric air |  |
| Dry O2 (%) |  |
| Boiler heat (kW) |  |
| Fuel-supported steam capacity (kg/s) |  |
| Adequacy (%) |  |
| Fuel/feedwater warning |  |

## Analysis and discussion questions

Why should volumetric fuel-flow values not be compared directly with mass-flow values?

How does the model represent the effect of lower LHV at unchanged commanded fuel flow?

Why can a fuel-quality loss reduce steam capability before drum level changes greatly?

What additional real-plant information would be needed before making an engineering fuel-conversion decision?

## Expected qualitative behaviour

Different fuels produce different air demand and heat release for the same user-entered flow basis.

A reduced LHV lowers boiler heat and fuel-supported steam capacity.

Adequacy falls and a delayed fuel/feedwater warning may appear if feedwater exceeds energy-supported evaporation.

Automatic controls mitigate but cannot create missing fuel energy.

Exercise 4: Load Step, Drum Shrink/Swell and Level-Control Modes

| Suggested duration | Format | Difficulty |
| --- | --- | --- |
| 60 min | Pairs | Intermediate |

## Learning objectives

Observe transient drum shrink/swell following steam-demand changes.

Compare single-, two- and three-element level-control concepts.

Explain why flow measurements improve level control during load changes.

## Initial setup

Reset and reach stable operation.

Use the Trends tab.

Perform the same disturbance separately under Single-element, Two-element and Three-element modes.

## Procedure

Select Single-element mode and clear trends.

Apply Demand +10% twice, observe for 40 simulated seconds, then record peak drum-level deviation and recovery behaviour.

Reset and repeat under Two-element mode.

Reset and repeat under Three-element mode.

Optionally repeat with Auto-select and note the selected mode.

## Data to record

| Variable / observation | Recorded value / notes |
| --- | --- |
| Control mode |  |
| Initial drum level (%) |  |
| Peak or minimum indicated level (%) |  |
| Steam-flow peak |  |
| Feedwater-flow response |  |
| Approximate recovery time |  |
| Presence of overshoot/oscillation |  |

## Analysis and discussion questions

Why can indicated drum level initially move in a direction not explained by inventory alone?

What extra information is used by two-element control? By three-element control?

Which mode responds most directly to a steam-flow disturbance in this simulator?

Why might a simpler mode be preferable at low load or with unreliable flow signals?

## Expected qualitative behaviour

Demand increase changes steam flow and produces a temporary swell/shrink contribution to indicated level.

Single-element control reacts mainly after level changes.

Two- and three-element strategies use steam flow, and three-element also closes the feedwater-flow loop.

Auto-select can simplify or fall back depending on load and transmitter quality.

Exercise 5: Cascade Steam-Temperature Control and Spray Response

| Suggested duration | Format | Difficulty |
| --- | --- | --- |
| 45-60 min | Pairs | Intermediate |

## Learning objectives

Describe outer and inner loops in cascade temperature control.

Observe how spray demand responds to steam-temperature disturbances.

Recognize the limits of control during severe firing-demand mismatch.

## Initial setup

Reset and stabilize.

Keep Auto cascade steam-T enabled initially.

Use the Trends and Alarms tabs.

## Procedure

Raise the steam-temperature setpoint by 30 C and observe mid-temperature, outlet temperature and spray command.

Return to the original setpoint and allow recovery.

Disable Auto cascade steam-T and repeat the disturbance with manual spray unchanged.

Reset, then inject Excess firing at low steam demand. Observe temperature, spray and possible trip behaviour.

## Data to record

| Variable / observation | Recorded value / notes |
| --- | --- |
| Control state (auto/manual) |  |
| Steam-T setpoint |  |
| Mid steam temperature |  |
| Final steam temperature |  |
| Spray command (%) |  |
| Time to approach setpoint |  |
| Alarm/trip status |  |

## Analysis and discussion questions

What is the role of the outer loop? What is the role of the inner loop?

Why is spray water effective for lowering superheated-steam temperature?

Why can coordinated firing reduce the severity of a load/firing mismatch?

Why can the controller still fail to prevent a trip during a sufficiently severe disturbance?

## Expected qualitative behaviour

Automatic cascade changes spray demand in response to temperature error.

Manual operation produces larger or longer deviations unless the student intervenes.

Excess firing at low demand raises steam-temperature stress and spray requirement.

A high-temperature master fuel trip may occur if the configured trip threshold is exceeded.

Exercise 6: Flow Measurement, Density Compensation and Controller Fallback

| Suggested duration | Format | Difficulty |
| --- | --- | --- |
| 60 min | Pairs | Intermediate |

## Learning objectives

Explain why differential-pressure flow measurements depend on fluid density.

Assess the effect of transmitter bias and noise on level-control mode selection.

Differentiate actual flow from measured/compensated flow.

## Initial setup

Reset and stabilize in Auto-select mode.

Keep the Measurements and Diagnostics panels visible.

## Procedure

Record actual and compensated steam and feedwater flows with Density compensation ON.

Turn Density compensation OFF and record the resulting indicated flows.

Turn compensation back ON and inject Steam-flow transmitter negative drift.

Observe the active control mode and the fallback message.

Clear the fault, then inject Feedwater-flow transmitter positive drift and repeat.

## Data to record

| Variable / observation | Recorded value / notes |
| --- | --- |
| Density compensation state |  |
| Steam actual flow |  |
| Steam compensated flow |  |
| FW actual flow |  |
| FW compensated flow |  |
| FT bias/noise settings |  |
| Selected/fallback mode |  |
| Drum-level response |  |

## Analysis and discussion questions

Why does density compensation matter more when fluid density changes?

How can a biased steam-flow signal mislead three-element control?

Why does the auto-selection logic fall back to simpler modes?

What independent checks would an operator use before trusting a suspect transmitter?

## Expected qualitative behaviour

Healthy compensated measurements approximately reproduce actual flow.

Removing compensation changes inferred mass flow from the DP relationship.

Severe steam- or feedwater-transmitter faults trigger automatic fallback logic.

The simulator demonstrates control robustness concepts, not detailed transmitter calibration.

Exercise 7: Tube Fouling, Stack Temperature and Dew-Point Margin

| Suggested duration | Format | Difficulty |
| --- | --- | --- |
| 45-60 min | Pairs | Intermediate |

## Learning objectives

Relate heat-transfer degradation to stack temperature and boiler efficiency.

Interpret stack-to-water-dew-point margin.

Separate a fouling signature from an excess-air signature.

## Initial setup

Reset and stabilize at normal excess air.

Keep air leakage at 0% and burner mixing at 95%.

Use the Flue Gas and Alarms tabs.

## Procedure

Set tube fouling successively to 0%, 25%, 50% and 75%.

At each point, record effective heat capture, stack temperature, efficiency and steam capacity.

Restore fouling to 0%, then raise excess air to 45% and compare the signature.

Select a wet fuel condition by setting fuel moisture to 30% or inject the Wet fuel fault. Record dew point and margin.

## Data to record

| Variable / observation | Recorded value / notes |
| --- | --- |
| Fouling (%) |  |
| Effective heat capture |  |
| Stack temperature (C) |  |
| Efficiency (%) |  |
| Steam capacity (kg/s) |  |
| Water dew point (C) |  |
| Dew-point margin (C) |  |
| Diagnosis |  |

## Analysis and discussion questions

Why does fouling raise stack temperature?

How can excess air also raise stack temperature, and how would O2 help distinguish the causes?

Why does added fuel moisture raise water dew point?

What does a small positive dew-point margin imply operationally?

Which simulator result should not be treated as a corrosion-design calculation?

## Expected qualitative behaviour

Fouling lowers effective heat capture and sends more energy to the stack.

Efficiency and steam capability fall as fouling increases.

High excess air is accompanied by elevated O2, whereas fouling need not be.

Wet fuel raises flue-water loading and reduces the stack-to-dew-point margin.

Exercise 8: Flue-Gas Fault Diagnosis Challenge

| Suggested duration | Format | Difficulty |
| --- | --- | --- |
| 60-75 min | Teams | Advanced |

## Learning objectives

Diagnose combustion and heat-transfer faults from multiple indicators.

Avoid relying on O2 alone.

Recommend an appropriate operator or maintenance response.

## Initial setup

One student acts as instructor and secretly selects a fault.

Other team members may view trends and indications but not the fault-selection box.

Use only one injected fault at a time.

## Procedure

Select among Air-starved firing, Excess air, Poor burner mixing, Post-furnace air leak, Flame quench/UHC, Tube fouling or Analyzer sluggish/noisy.

Run the scenario until a recognizable trend develops.

The diagnosing team states the fault, evidence, confidence level and recommended action.

Reveal the fault, clear it and repeat with roles exchanged.

Complete at least four scenarios.

## Data to record

| Variable / observation | Recorded value / notes |
| --- | --- |
| Scenario number |  |
| Observed O2, CO2 and CO |  |
| NOx and UHC |  |
| Stack temperature |  |
| Efficiency |  |
| Analyzer dynamics |  |
| Suspected fault |  |
| Evidence |  |
| Recommended action |  |
| Actual fault |  |

## Analysis and discussion questions

Why is high O2 not proof that the burner itself has enough air?

What distinguishes poor mixing from simple air starvation?

How does analyzer lag affect the timing of diagnosis?

Which fault primarily affects heat transfer rather than combustion chemistry?

For each scenario, identify one misleading indication.

## Expected qualitative behaviour

Air starvation: low O2 and high CO.

Excess air: high O2, diluted CO2, higher stack loss and generally low CO.

Poor mixing: high CO despite not-extremely-low O2.

Post-furnace leakage: measured O2 rises while CO2 and CO are diluted.

Fouling: high stack temperature and reduced heat capture without a matching combustion-air explanation.

Exercise 9: NOx-UHC-CO Trade-offs

| Suggested duration | Format | Difficulty |
| --- | --- | --- |
| 60 min | Pairs or groups | Advanced |

## Learning objectives

Interpret simplified NOx and UHC estimates as trend indicators.

Explore trade-offs among excess air, mixing, fuel nitrogen, CO, UHC and efficiency.

Explain why emissions optimization is multi-objective.

## Initial setup

Reset.

Use the Flue Gas tab.

Keep in mind that NOx and UHC outputs are teaching estimates, not regulatory predictions.

## Procedure

Record a clean baseline.

Increase fuel nitrogen from 0.05 wt% to 0.5%, 1.0% and 1.5%.

Restore fuel nitrogen, then reduce burner mixing to 70% and 50%.

At each condition, record NOx, corrected NOx, UHC, CO, O2 and efficiency.

Try one combined adjustment that lowers NOx without causing excessive CO or UHC.

## Data to record

| Variable / observation | Recorded value / notes |
| --- | --- |
| Fuel nitrogen (wt%) |  |
| Burner mixing (%) |  |
| Excess air (%) |  |
| NOx dry (ppm) |  |
| NOx corrected to 3% O2 |  |
| UHC (ppmC) |  |
| CO (ppm) |  |
| O2 (%) |  |
| Efficiency (%) |  |

## Analysis and discussion questions

Why is NOx corrected to a reference O2 concentration?

Which NOx contribution responds directly to fuel nitrogen in this model?

Why can aggressively reducing flame-temperature or oxygen conditions increase CO/UHC?

Why should corrected and uncorrected emissions both be examined?

Propose a balanced operating strategy and state its compromises.

## Expected qualitative behaviour

Increasing fuel nitrogen raises the fuel-NOx contribution.

Poor mixing raises CO and UHC and may alter NOx trends.

O2 correction reduces dilution bias when comparing NOx readings.

No single adjustment simultaneously minimizes NOx, CO, UHC and stack loss under all conditions.

Teaching note: Explicitly require students to state that these emissions values are reduced-order teaching estimates.

Exercise 10: Open-Ended Boiler Optimization and Operating Envelope

| Suggested duration | Format | Difficulty |
| --- | --- | --- |
| 90-120 min | Groups of 3-4 | Advanced |

## Learning objectives

Integrate combustion, heat transfer, steam production, control and emissions considerations.

Define constraints and optimize a multi-variable operating point.

Communicate assumptions, trade-offs and limitations.

## Initial setup

Choose one fuel and a steam-demand factor between 0.8 and 1.2.

Reset and enable CSV logging.

The instructor may impose one hidden degradation or instrument fault.

## Procedure

Define an objective such as maximizing efficiency while keeping O2, CO, NOx, UHC, drum level, steam temperature and dew-point margin within stated limits.

Select numerical acceptance limits before changing controls.

Adjust only physically meaningful variables such as excess air/O2 setpoint, burner mixing, coordinated firing, spray control and feedwater mode.

Run at least three candidate operating points and export the log.

Select the best operating point and defend the choice.

Inject or reveal one fault and demonstrate whether the chosen strategy remains acceptable.

## Data to record

| Variable / observation | Recorded value / notes |
| --- | --- |
| Chosen fuel and demand |  |
| Decision variables |  |
| Constraint limits |  |
| Candidate 1 results |  |
| Candidate 2 results |  |
| Candidate 3 results |  |
| Selected operating point |  |
| Fault response |  |
| Final recommendation |  |

## Analysis and discussion questions

What objective function did your group use?

Which constraints became active first?

Which variable had the strongest effect on efficiency? On CO? On drum stability?

How robust was the optimum to the injected fault?

Which simulator simplifications limit transfer of the optimum to a real boiler?

What additional measurements or models would be required for plant implementation?

## Expected qualitative behaviour

A defensible solution balances efficiency, stable steam production, acceptable combustion indicators and control margin.

The optimum is constrained by competing goals rather than one maximum or minimum.

A robust operating point retains margin against faults and measurement uncertainty.

Conclusions explicitly distinguish educational trends from real-plant design or regulatory analysis.

Exercise 11: Reading the Live Energy Sankey

| Suggested duration | Format | Difficulty |
| --- | --- | --- |
| 45-60 min | Pairs | Intermediate |

## Learning objectives

Interpret the direction and magnitude of the Sankey energy streams.

Connect fuel input, useful boiler heat and individual losses to efficiency.

Check whether the displayed energy balance closes within the reduced-order model.

## Initial setup

Reset and stabilize on Natural Gas with coordinated firing enabled.

Open the Energy Sankey, Trends and Diagnostics tabs.

Keep excess air, fouling and fuel moisture at their baseline values initially.

## Procedure

Record the baseline fuel input, boiler heat, wall loss, stack loss, incomplete-combustion loss, moisture loss, ash loss and balance residual.

Raise excess air to 45%, allow the response to settle and record the changed Sankey streams.

Restore excess air, inject Tube fouling and compare the redistribution of useful heat and stack loss.

Inject Wet fuel and identify which displayed loss pathway changes most directly.

For each case, calculate useful heat divided by fuel input and compare it with displayed efficiency.

## Data to record

| Variable / observation | Recorded value / notes |
| --- | --- |
| Fuel heat input (kW) |  |
| Useful boiler heat (kW) |  |
| Wall loss (kW) |  |
| Stack loss (kW) |  |
| Incomplete-combustion loss (kW) |  |
| Moisture/ash losses (kW) |  |
| Balance residual (kW) |  |
| Displayed/calculated efficiency (%) |  |
| Fault or adjustment |  |

## Analysis and discussion questions

Why must every Sankey outflow be interpreted on the same energy basis?

Which loss responds most clearly to excess air, fouling and wet fuel respectively?

Why is a small balance residual acceptable numerically but a large residual diagnostically important?

Which Sankey values are modeled estimates rather than direct plant measurements?

## Expected qualitative behaviour

Higher excess air increases flue-gas sensible loss and can reduce efficiency.

Fouling shifts energy away from useful heat capture and toward the stack.

Wet fuel increases the moisture-related burden and can reduce steam capability.

The Sankey approximately closes because its streams are generated from the same model energy balance.

Teaching note: Treat arrow widths as a live visualization of the simplified balance, not as a substitute for a plant heat-loss test.

Exercise 12: Fuel-Feedwater Mismatch and Eventual Drum Fill

| Suggested duration | Format | Difficulty |
| --- | --- | --- |
| 45-60 min | Pairs | Intermediate |

## Learning objectives

Relate fuel-supported steam capacity to feedwater flow and drum inventory.

Recognize the delayed low-fuel-for-feedwater warning before a large level excursion develops.

Separate transient shrink/swell indication from sustained inventory accumulation.

## Initial setup

Reset, stabilize and keep three-element or Auto-select level control enabled.

Display Trends, Diagnostics and Alarms together where practical.

Record the configured fuel/feedwater warning margin and delay.

## Procedure

Record the baseline fuel-supported steam capacity, steam flow, feedwater flow, drum inventory/level and adequacy.

Apply Fuel quality -5% repeatedly or inject a low-fuel condition while holding steam demand and feedwater conditions initially unchanged.

Observe the warning timer, fuel/feedwater adequacy and the longer-term drum-level direction.

Compare the short shrink/swell response with the sustained inventory trend.

Recover by restoring fuel quality or matching feedwater and firing, then document the response sequence.

## Data to record

| Variable / observation | Recorded value / notes |
| --- | --- |
| Fuel-supported steam capacity (kg/s) |  |
| Actual steam flow (kg/s) |  |
| Feedwater flow (kg/s) |  |
| Fuel/feedwater adequacy (%) |  |
| Warning timer/status |  |
| Drum inventory/level (%) |  |
| Shrink/swell contribution |  |
| Recovery action |  |
| Recovery time (s) |  |

## Analysis and discussion questions

Why can drum inventory rise when insufficient fuel is available?

Why is the warning delayed rather than activated by one noisy sample?

Which measurements distinguish a temporary swell from genuine mass accumulation?

What operator action is educationally appropriate, and what real-plant safeguards are outside this simulator?

## Expected qualitative behaviour

Reduced fuel energy lowers evaporation capability before drum level changes dramatically.

If feedwater exceeds energy-supported steam generation, inventory trends upward and the warning eventually activates.

Shrink/swell decays as a transient indication, while a true mass imbalance persists.

Restoring the energy/flow balance arrests the inventory drift; controller action cannot manufacture missing heat.

Teaching note: This is an inventory-control exercise. It does not model every real drum-boiler protection, trip or startup permissive.

Exercise 13: Alarm Chronology, Trend Timebase and Analyzer Lag

| Suggested duration | Format | Difficulty |
| --- | --- | --- |
| 60 min | Teams of 3 | Advanced |

## Learning objectives

Read rolling trend x-axes correctly as simulated seconds before present.

Build a cause-and-effect chronology from process variables, analyzer outputs, alarms and controller responses.

Explain why analyzer lag can delay or distort fault diagnosis.

## Initial setup

Reset, clear trends and select 1x speed.

Set analyzer lag to 8 s for the first run and note the configured alarm thresholds.

Assign operator, recorder and diagnostician roles.

## Procedure

Inject Air-starved firing and record the simulated time at which O2, CO and the alarm first show a clear response.

Clear the fault, repeat with analyzer lag near its minimum and compare detection order and delay.

Repeat using Wet fuel or High fuel-nitrogen/NOx excursion and track dew-point or NOx alarm chronology.

Explain why the newest sample is at zero seconds before present and older samples appear toward the negative/earlier side of the rolling window.

Prepare a one-minute incident briefing stating initiating event, first reliable symptom, controller response, alarm and recommended action.

## Data to record

| Variable / observation | Recorded value / notes |
| --- | --- |
| Fault and injection time (sim s) |  |
| First process response |  |
| First analyzer response |  |
| Alarm annunciation time |  |
| O2/CO/NOx/UHC response |  |
| Dew-point margin |  |
| Controller/mode response |  |
| Diagnosis and confidence |  |
| Recommended action |  |

## Analysis and discussion questions

Which variables respond as process states and which are delayed analyzer indications?

How does analyzer lag change diagnosis without changing the underlying combustion state?

Why should alarm order not automatically be interpreted as causal order?

Which paired indications provide the strongest evidence for each injected fault?

How would a different simulation-speed setting affect wall-clock observation but not simulated-time chronology?

## Expected qualitative behaviour

Process and controller variables can move before lagged flue-gas analyzer values.

Lower analyzer lag shortens indicated detection time but does not alter the modeled fault itself.

The rolling x-axis represents simulated time relative to the present, not sample number.

A defensible diagnosis combines chronology with multiple physically related indications.

Teaching note: Use one principal fault at a time for assessment. Combined faults may be used only after students establish the individual signatures.

# Instructor Appendix: Suggested Exercise Sequence

| Teaching format | Recommended selection |
| --- | --- |
| Single 2-hour class | Exercises 1 and 2, followed by selected fault demonstrations from Exercise 8 or the chronology activity in Exercise 13. |
| Three-hour laboratory | Exercises 1, 4 and 6, with Exercise 12 as an inventory-control extension. |
| Combustion laboratory | Exercises 2, 3, 7, 9 and selected Sankey comparisons from Exercise 11. |
| Controls laboratory | Exercises 4, 5, 6, 12 and 13. |
| Capstone mini-project | Exercise 10 supported by Exercises 11-13 and CSV analysis, followed by a group presentation. |

# General marking guidance

Award credit for physically coherent interpretation rather than exact agreement with a single number.

Require students to identify whether a variable is a true model state, a measured/analyzer value, a control command or a simplified diagnostic estimate.

Penalize conclusions that treat the simulator as CFD, a complete IAPWS-IF97 implementation, a regulatory emissions model or a plant-safety analysis tool.

Encourage students to use paired evidence: for example O2 with CO, stack temperature with O2, or drum level with steam/feedwater flow.

For group work, assign rotating roles such as operator, recorder, diagnostician and reviewer.

# Source and scope note

These exercises were derived from the controls, calculations, fault cases, alarm logic, time-based trends, live Energy Sankey and logging functions implemented in Live Boiler/Furnace Transient Simulator v1.2.0. The simulator states that its water/steam property helpers are simplified approximations informed by IAPWS-IF97, and that its NOx and UHC calculations are teaching-level trend models rather than regulatory predictions.